## Sheet1
id | pag | type | equipment | problem | cause | action
0 | 1 | mechanical | pumps | pump too hot and flashing off | unloading valve not working properly | repair or replace the unloading valve
1 | 1 | mechanical | pumps | pump too hot and flashing off | excessive wear in pump | repair or replace the pump
2 | 1 | mechanical | pumps | pump too hot and flashing off | relief valve set too high | adjust the relief valve
3 | 1 | mechanical | pumps | pump too hot and flashing off | discharge valve throttled or closed | open the discharge valve
4 | 1 | mechanical | pumps | pump churning up fluid and failing to discharge water after an initial surge, and then continuing to recirculate | leak in suction pipe | inspect the line for broken or loose connections to determine the source of the leak
5 | 2 | mechanical | pumps | pump churning up fluid and failing to discharge water after an initial surge, and then continuing to recirculate | packing or seal worn | inspect the line for broken or loose connections to determine the source of the leak
6 | 2 | mechanical | pumps | pump churning up fluid and failing to discharge water after an initial surge, and then continuing to recirculate (continued) | lift too great | report this as an engineering problem; it may require design changes. clean filters
7 | 3 | mechanical | pumps | pump churning up fluid and failing to discharge water after an initial surge, and then continuing to recirculate (continued) | discharge line blocked | report this as an engineering problem; it may require design changes. clean filters
8 | 3 | mechanical | pumps | pump churning up fluid and failing to discharge water after an initial surge, and then continuing to recirculate (continued) | choked up filter | report this as an engineering problem; it may require design changes. clean filters
9 | 2 | mechanical | pumps | pump churning up fluid and failing to discharge water after an initial surge, and then continuing to recirculate (continued) | suction pipe too long | report this as an engineering problem; it may require design changes
10 | 2 | mechanical | pumps | pump churning up fluid and failing to discharge water after an initial surge, and then continuing to recirculate (continued) | insufficient head | increase the supply source level
11 | 2 | mechanical | pumps | pump churning up fluid and failing to discharge water after an initial surge, and then continuing to recirculate (continued) | suction valve shut | increase the supply source level
12 | 2 | mechanical | pumps | pump churning up fluid and failing to discharge water after an initial surge, and then continuing to recirculate (continued) | too much air in the system | check the suction system and glands for air ingress. if the source is from a pond, check to see if there are any whirlpools sucking air into the system. throttle the pump to reduce the rate of withdrawal from the supply source
13 | 3 | mechanical | pumps | heavy vibrations during the operation of the pump | pump and motor out of alignment | perform vibration analysis to determine the source of the problem(s). mechanical maintenance should conduct alignment checks and make the necessary adjustments
14 | 3 | mechanical | pumps | heavy vibrations during the operation of the pump | bent shaft | perform vibration analysis to determine the source of the problem(s). mechanical maintenance should conduct alignment checks and make the necessary adjustments
15 | 3 | mechanical | pumps | heavy vibrations during the operation of the pump | cavitation | perform vibration analysis to determine the source of the problem(s). mechanical maintenance should conduct alignment checks and make the necessary adjustments
16 | 3 | mechanical | pumps | heavy vibrations during the operation of the pump | recirculation | perform vibration analysis to determine the source of the problem(s). mechanical maintenance should conduct alignment checks and make the necessary adjustments
17 | 3 | mechanical | pumps | heavy vibrations during the operation of the pump | unusual wear | perform vibration analysis to determine the source of the problem(s). mechanical maintenance should conduct alignment checks and make the necessary adjustments
18 | 3 | mechanical | pumps | heavy vibrations during the operation of the pump | some rotating element broken off, causing an unbalanced condition | perform vibration analysis to determine the source of the problem. mechanical maintenance should conduct balancing corrections
19 | 4 | mechanical | pumps | heavy vibrations during the operation of the pump (continued) | cavitation from lack of net positive suction head or turbulence from sharp pipe bends immediately upstream of the pump | lower the suction temperature
20 | 4 | mechanical | pumps | heavy vibrations during the operation of the pump (continued) | suction pressure lower than the corresponding saturation temperature | lower the suction temperature
21 | 4 | mechanical | pumps | heavy vibrations during the operation of the pump (continued) | recirculation due to blocked or narrowed discharge line | increase the clearance at the exit tips of vanes to eliminate and avoid discharge restrictions
22 | 4 | mechanical | pumps | heavy vibrations during the operation of the pump (continued) | obstruction lodged in one side of the impeller | have maintenance open the pump casing and remove any obstruction that may be there. check to ensure that there is no further damage
23 | 5 | mechanical | pumps | heavy vibrations during the operation of the pump (continued) | lack of lubricant or over-lubrication | inspect the oil well sight glasses, or check the dipsticks. add lubricant as necessary. determine if the proper grade of lubricant is being used. change the lubricant if necessary
24 | 5 | mechanical | pumps | heavy vibrations during the operation of the pump (continued) | pump not turned regularly when sitting idle | the pump should be turned frequently when it is on standby to avoid false brinelling and other surface defects on bearings
25 | 5 | mechanical | pumps | heavy vibrations during the operation of the pump (continued) | incorrect installation | contact mechanical maintenance to have the installation checked
26 | 6 | mechanical | pumps | capacity or pressure of the pump reduced | wrong direction of rotation | check the direction of the arrow that is usually cast on the casing to verify the rotation direction. have electricians check the wiring connections and correct them
27 | 6 | mechanical | pumps | capacity or pressure of the pump reduced | discharge line blocked | check the direction of the arrow that is usually cast on the casing to verify the rotation direction. have electricians check the wiring connections and correct them
28 | 6 | mechanical | pumps | capacity or pressure of the pump reduced | discharge valve closed | check the direction of the arrow that is usually cast on the casing to verify the rotation direction. have electricians check the wiring connections and correct them
29 | 6 | mechanical | pumps | capacity or pressure of the pump reduced | impeller mounted incorrectly | have mechanical maintenance verify the impeller mounting and reverse the impeller on the shaft
30 | 6 | mechanical | pumps | capacity or pressure of the pump reduced | mechanical defects, such as worn rings, damaged impeller, or a defective casing gasket | have maintenance verify and correct the problem
31 | 6 | mechanical | pumps | capacity or pressure of the pump reduced | clogged filters | check the pressure differential across the filter. if the differential is too high, change and clean filters
32 | 6 | mechanical | pumps | pump failing to deliver water | wrong direction of rotation | check the direction of the arrow that is usually cast on the casing to verify the rotation direction. have electricians check the wiring connections and correct them
33 | 6 | mechanical | pumps | pump failing to deliver water | discharge line blocked | check the direction of the arrow that is usually cast on the casing to verify the rotation direction. have electricians check the wiring connections and correct them
34 | 6 | mechanical | pumps | pump failing to deliver water | discharge valve closed | check the direction of the arrow that is usually cast on the casing to verify the rotation direction. have electricians check the wiring connections and correct them
35 | 6 | mechanical | pumps | pump failing to deliver water | impeller mounted incorrectly | have mechanical maintenance verify the impeller mounting and reverse the impeller on the shaft
36 | 6 | mechanical | pumps | pump failing to deliver water | mechanical defects, such as worn rings, damaged impeller, or a defective casing gasket | have maintenance verify and correct the problem
37 | 6 | mechanical | pumps | pump failing to deliver water | clogged filters | check the pressure differential across the filter. if the differential is too high, change and clean filters
38 | 7 | mechanical | pumps | motor using excessive power at rated temperature | required differential head or pressure lower than rated | throttle the discharge valve until the rated capacity is reached
39 | 7 | mechanical | pumps | motor protection relay being tripped by the pump | required differential head or pressure lower than rated | throttle the discharge valve until the rated capacity is reached
40 | 8 | mechanical | pumps | bearings running hot | improper alignment | perform phase angle analysis to determine piping misalignment. perform soft-foot analysis. check to see if the correct grease is used and correct application. determine if the bearing was installed per manufacturer's procedure
41 | 8 | mechanical | pumps | bearings running hot | piping misalignment | perform phase angle analysis to determine piping misalignment. perform soft-foot analysis. check to see if the correct grease is used and correct application. determine if the bearing was installed per manufacturer's procedure
42 | 8 | mechanical | pumps | bearings running hot | bent shaft | perform phase angle analysis to determine piping misalignment. perform soft-foot analysis. check to see if the correct grease is used and correct application. determine if the bearing was installed per manufacturer's procedure
43 | 8 | mechanical | pumps | bearings running hot | poor lubrication | perform phase angle analysis to determine piping misalignment. perform soft-foot analysis. check to see if the correct grease is used and correct application. determine if the bearing was installed per manufacturer's procedure
44 | 8 | mechanical | pumps | bearings running hot | over-greasing | perform phase angle analysis to determine piping misalignment. perform soft-foot analysis. check to see if the correct grease is used and correct application. determine if the bearing was installed per manufacturer's procedure
45 | 8 | mechanical | pumps | bearings running hot | poor foundations | perform phase angle analysis to determine piping misalignment. perform soft-foot analysis. check to see if the correct grease is used and correct application. determine if the bearing was installed per manufacturer's procedure
46 | 8 | mechanical | pumps | bearings running hot | improperly fitted bearings | perform phase angle analysis to determine piping misalignment. perform soft-foot analysis. check to see if the correct grease is used and correct application. determine if the bearing was installed per manufacturer's procedure
47 | 9 | mechanical | pumps | bearings running hot (continued) | bearing substitute used and never replaced with original specification model | use the maintenance management tracking system to see if the bearing was replaced in an emergency with a substitute bearing because it was
48 | 9 | mechanical | pumps | insufficient discharge | air leaks in suction line or stuffing box | close enough
49 | 9 | mechanical | pumps | insufficient discharge | wear rings worn or damaged | and the substitute was never replaced with the correct one
50 | 9 | mechanical | pumps | insufficient discharge | foot valve too small | tighten the glands slightly. check the suction line for leaks
51 | 10 | mechanical | pumps | excessive power consumption | speed too high | replace wear rings. determine correct wear ring clearances
52 | 10 | mechanical | pumps | excessive power consumption | specific gravity or viscosity too high | replace wear rings. determine correct wear ring clearances
53 | 10 | mechanical | pumps | excessive power consumption | bent shaft | determine the proper size of the foot valve
54 | 10 | mechanical | pumps | excessive power consumption | rotating element binds | determine the correct speed and specific gravity or viscosity. a design change may be required
55 | 10 | mechanical | pumps | excessive power consumption | stuffing boxes too tight | replace the shaft
56 | 10 | mechanical | pumps | excessive power consumption | wearing rings worn | remove the shaft and inspect
57 | 11 | mechanical | bearings | overheating | wrong type of grease or oil causing breakdown of the lubricant | loosen the gland slightly if the stuffing box is too tight
58 | 11 | mechanical | bearings | overheating | low oil level | replace the rings
59 | 11 | mechanical | bearings | overheating | loss of oil through the seal | replace the rings
60 | 11 | mechanical | bearings | overheating | housing overpacked with grease, causing excessive churning of the lubricant | consult with the lubricant manufacturer to verify the correct grade of lubricant, and replace the old grease or oil with the correct one
61 | 11 | mechanical | bearings | overheating | inadequate internal clearance from using a substitute bearing | add oil until the oil level is just below the center of the lowest ball or roller in the bearing
62 | 12 | mechanical | bearings | overheating (continued) | housing bore out of round | purge the bearing until only the lower half is 1/2 to 2/3 full of grease
63 | 12 | mechanical | bearings | overheating (continued) | housing warped | purge the bearing until only the lower half is 1/2 to 2/3 full of grease
64 | 12 | mechanical | bearings | overheating (continued) | rotating seals rubbing against stationary parts | replace with a bearing that meets the original design specification
65 | 12 | mechanical | bearings | overheating (continued) | blocked oil return holes | determine what the true bore is and scrape the housing to relieve the pinching of the bearing
66 | 12 | mechanical | bearings | overheating (continued) | unbalanced load | check the running clearance of the rotating seal to eliminate rubbing. check the alignment of the bearing
67 | 12 | mechanical | bearings | overheating (continued) | housing bore too large | check the running clearance of the rotating seal to eliminate rubbing. check the alignment of the bearing
68 | 13 | mechanical | bearings | overheating (continued) | incorrect oil level causing insufficient oil to reach the bearing | clean the holes. investigate the type of debris
69 | 13 | mechanical | bearings | overheating (continued) | wrong type of lubricant, which has broken down and lost its lubricating properties | rebalance the machine. replace the housing with one having the correct size bore
70 | 14 | mechanical | bearings | noisy bearing. irregular dents or material embedded in raceways | foreign matter such as dirt, sand, and carbon entering the bearing housing | clean the clogged holes to vent the oil gauge. ensure bearing material is not the clogging agent. if it is, the bearing may have to be overhauled or replaced
71 | 14 | mechanical | bearings | noisy bearing. irregular dents or material embedded in raceways | brinnelling | check oil specs for the machine, and use the correct grade of lubricant
72 | 14 | mechanical | bearings | noisy bearing. irregular dents or material embedded in raceways | static electrical arcing in the bearings | clean out the bearing housing. replace any worn seals
73 | 15 | mechanical | bearings | noisy bearing (continued). irregular dents or material embedded in raceways | corrosive agents entering the bearing | rotate shafts 1/4 turn in all stationary machines at least once per two weeks
74 | 15 | mechanical | bearings | noisy bearing (continued). irregular dents or material embedded in raceways | failure to remove foreign matter from the bearing housing before assembling the bearing unit | ensure insulation and grounding gear are in good order
75 | 15 | mechanical | bearings | noisy bearing (continued). irregular dents or material embedded in raceways | a flat on a ball or a roller due to skidding | add a shroud or a finger to throw off any foreign matter
76 | 16 | mechanical | bearings | noisy bearing (continued). irregular dents or material embedded in raceways | incorrectly mounted bearing | carefully clean the housing and always use fresh lubricant
77 | 16 | mechanical | bearings | noisy bearing (continued). irregular dents or material embedded in raceways | bearing hammered onto the shaft or into the housing | carefully clean the housing and always use fresh lubricant
78 | 16 | mechanical | bearings | noisy bearing (continued). irregular dents or material embedded in raceways | interference of other movable parts of the machine | replace the bearing
79 | 16 | mechanical | bearings | noisy bearing (continued). irregular dents or material embedded in raceways | unbalanced load | replace the bearing without hammering any part of it. use a press to install the bearing or uniformly heat or chill bearing to set it
80 | 16 | mechanical | bearings | noisy bearing (continued). irregular dents or material embedded in raceways | housing bore too large | replace the bearing without hammering any part of it. use a press to install the bearing or uniformly heat or chill bearing to set it
81 | 16 | mechanical | bearings | noisy bearing (continued). irregular dents or material embedded in raceways | bearing exposed to resonance-caused vibration while the machine is idle | check every moving part for interference. reset the parts to provide the necessary clearance
82 | 17 | mechanical | bearings | vibration | distortion of shaft and inner ring | rebalance the unit. replace the housing with one that has the correct size bore
83 | 17 | mechanical | bearings | vibration | distortion of the housing and outer ring, causing pinching of the bearing | carefully examine the bearing for wear spots that are separated by the distance equal to the spacing of the balls. replace the bearings
84 | 17 | mechanical | bearings | vibration | rotating seals rubbing against stationary parts | remachine the shaft fillet to obtain the correct support
85 | 17 | mechanical | bearings | vibration | incorrectly mounted bearing as indicated by hammer blow signs on the bearing | remachine the housing fillet to obtain the correct support. check the manufacturer's tolerance measurement guides
86 | 17 | mechanical | bearings | vibration (continued) | inadequate support in the housing, causing the outer ring to cock | check the running clearance of the rotating seals to eliminate rubbing
87 | 18 | mechanical | bearings | vibration (continued) | general vibration of the machine | replace with a new bearing without hammering it into place. follow the bearing manufacturer's fitting recommendations
88 | 18 | mechanical | bearings | vibration (continued) | shaft and housing shoulders and face of the locking nut not square with the bearing seat | remachine the housing fillet to relieve stress. remachining may require a shoulder collar
89 | 19 | mechanical | bearings | bearing loose on the shaft | shaft diameter too small or adapter not tight enough | check the balance of the machine. rebalance the machine if necessary
90 | 19 | mechanical | bearings | bearing loose on the shaft | knurling and center punching of the bearing seat on the shaft, causing the high spots to be flattened when the load is applied | remachine the parts to obtain squareness. ensure that there is a radius machined in at the root of the shoulder to minimize stress riser
91 | 19 | mechanical | bearings | bearing loose on the shaft | loose fitting shaft | remachine the parts to obtain squareness. ensure that there is a radius machined in at the root of the shoulder to minimize stress riser
92 | 20 | mechanical | bearings | shaft difficult to turn by hand | inadequate shoulder support in the housing causing bending of the shaft | metalize the shaft, and regrind it to obtain a proper fit. retighten the adapter to get a firmer grip on the shaft
93 | 20 | mechanical | bearings | shaft difficult to turn by hand | distortion of the bearing seals | metallize and regrind the shaft to the proper size. stress relieve shaft before putting it back into service
94 | 20 | mechanical | bearings | shaft difficult to turn by hand | bearing seat diameter machined oversize, causing excessive expansion of the shaft and bearing inner ring, thus reducing the clearance in the bearing | remachine the shaft fillet to relieve stress. this may require a shoulder collar to be fitted
95 | 21 | mechanical | bearings | shaft difficult to turn by hand | incorrect linear or angular alignment of two or more coupled shafts with two or more bearings | remachine the housing shoulder to clear the seal
96 | 21 | mechanical | bearings | shaft difficult to turn by hand | distortion of the housing and the outer ring causing pinching of the bearing | grind and hone the shaft to obtain a proper fit between the inner ring of the bearing and the shaft
97 | 21 | mechanical | bearings | angular misalignment | incorrect linear or angular alignment of two or more coupled shafts with two or more bearings | remachine the housing shoulder to clear the seal
98 | 21 | mechanical | bearings | angular misalignment | distortion of the housing and the outer ring causing pinching of the bearing | grind and hone the shaft to obtain a proper fit between the inner ring of the bearing and the shaft
99 | 21 | mechanical | bearings | frequent replacements | unequal load distribution on the bearing | shim the pillow blocks to correct the alignment. ensure that the shafts are coupled in a straight line. this is especially important when three or more bearings operate on one shaft
100 | 22 | mechanical | bearings | oil leakage | air flowing over the bearings, for example, a forced draft fan with air inlet over the bearings | remachine the housing fillet to obtain the proper support
101 | 22 | mechanical | bearings | oil leakage | oil leakage at the housing split causing excessive loss of lubricant | rework the shaft, the housing, or both to obtain a proper fit. a new shaft may be required
102 | 22 | mechanical | bearings | oil leakage | failure to remove debris from the bearing housing before assembling the bearing unit | provide adequate baffling to divert the direction of the airflow
103 | 23 | mechanical | valves | valve gland leakage | packing too loose | use a thin layer of gasket cement to seal off the leakage. shutdown the equipment if the leakage is excessive
104 | 23 | mechanical | valves | valve gland leakage | packing reached the end of its useful life | always carefully clean the housing and use fresh lubricant
105 | 23 | mechanical | valves | valve gland leakage | insufficient number of turns of packing | tighten the packing enough to stop the leak
106 | 23 | mechanical | valves | valve gland leakage | packing ring butts all in line | repack the gland with new, correctly sized packing rings
107 | 23 | mechanical | valves | valve gland leakage | valve stem badly scored | check the number of packing rings that should be in the gland. repack the gland with sufficient turns
108 | 24 | mechanical | valves | valve gland leakage (continued) | wrong grade packing material | stagger the ring butts by placing the first at 0°, the next at 180°, and then a 90°-270°. repeat the rotating sequence until the stuffing box is filled
109 | 24 | mechanical | valves | valve gland leakage (continued) | cocked gland follower | replace the valve stem. check why it is scored first
110 | 25 | mechanical | valves | body to bonnet gasket leakage | gasket beyond the 60% crush factor | replace with the correct grade
111 | 25 | mechanical | valves | body to bonnet gasket leakage | wrong type of gasket material | replace with the correct grade
112 | 25 | mechanical | valves | body to bonnet gasket leakage | hammer-cut gasket and fibers destroyed | adjust the gland follower to correctly place the follower at a 90° angle to the stem axis
113 | 26 | mechanical | valves | body to bonnet gasket leakage (continued) | wrong gasket material | replace the gasket with a new one. smear the gasket surfaces with a suitable lubricant to help preserve it
114 | 26 | mechanical | valves | body to bonnet gasket leakage (continued) | gasket landing surfaces dirty | replace the gasket with a new one. smear the gasket surfaces with a suitable lubricant to help preserve it
115 | 26 | mechanical | valves | body to bonnet gasket leakage (continued) | gasket landing grooved by wire-drawing | replace the gasket with a new one. smear the gasket surfaces with a suitable lubricant to help preserve it
116 | 26 | mechanical | valves | body to bonnet gasket leakage (continued) | scored body or bonnet seal faces | replace the gasket. gaskets should always be cut with a circular cutter and holes put in using a belt punch
117 | 26 | mechanical | valves | body to bonnet gasket leakage (continued) | body/or bonnet bolts improperly tightened | replace with the correct gasket material. the most expensive material is not always the best. use the gasket material that is recommended for the application
118 | 27 | mechanical | valves | body to bonnet gasket leakage (continued) | gasket too old and pressure blown | replace with a new gasket. new gaskets should always be used for replacements. never reuse the old gasket
119 | 28 | mechanical | valves | gate valve difficult to operate | packing gland too tight | adjust the packing until the valve operates easily
120 | 28 | mechanical | valves | gate valve difficult to operate | too many turns of packing installed | check the drawing for the correct number of turns required, and adjust
121 | 28 | mechanical | valves | gate valve difficult to operate | piping misalignment | break the joint, and correctly realign the pipe to the valve. align piping with zero cold spring
122 | 28 | mechanical | valves | gate valve difficult to operate | bent valve stem | straighten the stem to +/- 0.002" tir max
123 | 28 | mechanical | valves | gate valve difficult to operate | wrong size handwheel or motor operator | check the specifications, and replace with the proper handwheel
124 | 29 | mechanical | valves | gate valve hard to operate (continued) | stem threads or nut damaged | clean the threads, using thread chaser
125 | 29 | mechanical | valves | gate valve hard to operate (continued) | thermal binding of valve closed | contact maintenance. to prevent this problem from occurring, avoid forcing the valve into the seat in high temperature systems
126 | 30 | mechanical | valves | gate valve hard to operate (continued) | piping misaligned | avoid twisting valve body, especially check valves, gate valves, and butterfly valves
127 | 30 | mechanical | valves | gate valve hard to operate (continued) | valve internals out of alignment due to body stresses caused when piping to valve is misaligned | avoid twisting valve body, especially check valves, gate valves, and butterfly valves
128 | 31 | mechanical | valves | gate valve chattering | valve being used to throttle flow | adjust the valve to fully open or fully closed. gate valves are not designed to control or throttle flow. do not use them for this function
129 | 31 | mechanical | valves | gate valve chattering | piping distortion due to loading or temperature distortion | install spring hangers, and check the valve to the piping nozzle alignment. piping to valve alignment should have zero-cold-spring. in other words, both connections should be perfectly aligned with each other with no stress
130 | 32 | mechanical | valves | gate valve chattering (continued) | partially open valve | open or shut the valve completely. the gate valve should always be fully open or shut
131 | 32 | mechanical | valves | gate valve chattering (continued) | natural vibration frequency being excited by some other natural or induced vibration frequency | change the mass by stiffening the valve. add a weight to the pipe as close as possible to the valve
132 | 32 | mechanical | valves | gate valve chattering (continued) | rising stem valve in confined space restricting full opening | change the valve for a non-rising stem valve
133 | 32 | mechanical | valves | gate valve chattering (continued) | stem lock nut on yoke loose | tighten the yoke nut
134 | 33 | mechanical | valves | leakage across the disc and seat in a globe valve | erosion across the seat face | caution: during throttling operations, do not close the valve far enough to induce a high-pitched screaming noise
135 | 33 | mechanical | valves | leakage across the disc and seat in a globe valve | reface the disc and seat, and lap to ensure good contact all around the faces | caution: during throttling operations, do not close the valve far enough to induce a high-pitched screaming noise
136 | 33 | mechanical | valves | leakage across the disc and seat in a globe valve | seat contact surface area too wide | machine the disc and seat to produce a very narrow contact band around the seat and disc faces. ideally, maintain a 0.5° differential angle between the seat and disc faces
137 | 33 | mechanical | valves | leakage across the disc and seat in a globe valve | incorrect valve in the system | change the valve immediately if the valve is rated at 200 wog and 125 s and is operating in a 400-psi steam system
138 | 34 | mechanical | valves | leakage across the disc and seat in a globe valve (continued) | incorrect valve in the system (continued) | warning: if the valve is overpressurized, it is dangerous to operate at this pressure. it should be operating at no more than 200 psi in a water, oil, or gas system, and no more than 125 psi in steam system
139 | 35 | mechanical | valves | intermittent leakage across the valve | disc cocking due to bent valve stem | remove the stem, and check the tir. straighten the valve stem
140 | 35 | mechanical | valves | intermittent leakage across the valve | disc sticking due to slightly off-center misalignment of bonnet stem threads | change the valve. check piping alignment to the valve body. piping should have zero cold spring with valve nozzle
141 | 35 | mechanical | valves | intermittent leakage across the valve | stem attached to the disc nut is too tight, restricting the disc from self-centering in the seat | add shims one at a time between the stem nut and disc shoulder until sufficient float is achieved
142 | 36 | mechanical | valves | screwed bonnet loosening off repeatedly | valve back-seated too tightly | retighten the bonnet lock nut. warning: if this problem is not corrected, the valve may blow out and cause injury. to avoid this problem, do not force the stem to the backseat against the cover, particularly using a valve wrench
143 | 37 | mechanical | valves | screwed bonnet loosening off repeatedly (continued) | missing lock screw or tab | verify the need for a lock screw or tab by reading the drawing or manufacturer"s documentation, and reinstall the tab or lock screw if necessary. warning: never install a screwed bonnet globe valve in a high-pressure system or a dangerous substance system because the bonnet can become unscrewed if it is forced against the backseat
144 | 37 | mechanical | valves | screwed bonnet loosening off repeatedly (continued) | bonnet lock nut not torqued to specified setpoints | verify the setting, using a torque wrench to correct the setting if required
145 | 38 | mechanical | valves | piping flange leaking | bolts improperly tightened | loosen the bolts, and retighten properly. flange bolts need to be tightened sequentially around the bolt pitch circle. after the first nut is tightened snugly, go 180° across to the second nut, and tighten it snugly. go 90° to the third nut, and tighten it snugly. go 180° to tighten the fourth nut. repeat this sequence until all the bolts are snugly tightened. torque all nuts to specification in the same sequence to complete the tightening process
146 | 39 | mechanical | valves | valve to piping flange leaking (continued) | reusing old gasket, causing old gasket material to stick to the flange surface | scrape the flange clean of all foreign material. ensure that the flange faces are properly aligned to each other and at the zero cold spring setpoint. always use a new gasket when installing a valve or making repairs
147 | 40 | mechanical | valves | valve to piping flange leaking (continued) | wrongly set flexible gasket | if the compression is less than 60% and no other damage is apparent, then tighten the gasket to the correct setpoint. if the compression is greater than 60%, scrap the gasket, and replace it with a new gasket. flexitallic gasket corrugations must be compressed to a minimum of 60% of the original thickness for effective sealing. if the gasket is compressed beyond 90%, it becomes ineffective
148 | 41 | mechanical | valves | pressure safety valve leaking | improper setting | correct the setting, or contact maintenance. warning: ensure that a gag is not left in place or being used to try to stop leakage across valve seat. pressure tests the valve to lift at 110% of the working pressure of the boiler
149 | 41 | mechanical | valves | pressure safety valve leaking | valve-disc-to-seat contact area too large, causing valve simmering to take place | reface the seat face and disc face to maintain a 1/2 degree angle differential between the points of contact
150 | 42 | mechanical | valves | pressure safety valve leaking (continued) | cracked or broken compression spring | perform a visual inspection of the spring for cracks or breaks. if the spring can be taken off valve without being broken, hang it on a string, and strike it very lightly with a peen hammer. if the spring rings loudly and clearly, it does not have a crack. if the spring makes a clunking sound, it is cracked. replace it
151 | 42 | mechanical | valves | pressure safety valve leaking (continued) | bent valve stem | check the stem tir to ensure that the stem is not bent. straighten the stem if necessary
152 | 43 | mechanical | valves | intermittent vibration on valves and associated piping | improper loading of pipe hangers | evaluate the current setpoints to ensure that they meet specifications
153 | 43 | mechanical | valves | intermittent vibration on valves and associated piping | resonance | remove anything that should not be on the piping. piping and valves may be loaded down with scaffolding or maintenance walkways. this can alter the mass, affecting the natural frequency and causing the scaffolding or walkways to vibrate in tune with a pump or motor having the same natural frequency. this vibration can have devastating results
154 | 43 | mechanical | valves | intermittent vibration on valves and associated piping | water hammer | ensure that the steam traps are operating and do not need maintenance. clean the traps as necessary. open the drain valves during any plant shutdown
155 | 44 | mechanical | valves | continual leakage across a butterfly valve | valve may be installed in the wrong direction | check the direction arrow casting on the side of valve body. reverse the body installation if the directional arrow indicates that the valve is incorrectly installed
156 | 44 | mechanical | valves | continual leakage across a butterfly valve | piping misalignment with valve | inspect and report the findings to maintenance. piping misalignment can distort the valve body and can cause the disc shaft trunnions to get out of alignment and bind up
157 | 44 | mechanical | valves | continual leakage across a butterfly valve | neoprene valve seat and gasket | check the valve seat to ensure that it did not kink or roll during installation. straighten as necessary
158 | 45 | mechanical | valves | hand-operated valve difficult to open | thread damage | take the stem out of the valve. and run a die-nut down the thread if it is a standard thread. if it is an acme thread, use a thread chaser or a fine file to remove any imperfections
159 | 45 | mechanical | valves | hand-operated valve difficult to open | shaft bent | remove the shaft, and check tir. straighten the shaft, and reinstall in the valve
160 | 45 | mechanical | valves | hand-operated valve difficult to open | valve body twisted | separate the pipe from the valve, and observe how far the pipe moves out of alignment. if the pipe is out of alignment, the pipe must be bent until it meets the valve nozzle with zero cold spring. warning: if a hand-operated valve cannot be moved without difficulty, it requires maintenance. never force a valve by using a wrench
161 | 45 | mechanical | valves | hand-operated valve difficult to open | piping misaligned to valve body | separate the pipe from the valve, and observe how far the pipe moves out of alignment. if the pipe is out of alignment, the pipe must be bent until it meets the valve nozzle with zero cold spring. warning: if a hand-operated valve cannot be moved without difficulty, it requires maintenance. never force a valve by using a wrench
162 | 46 | mechanical | valves | hand-operated valve difficult to open | bonnet stem nut out of alignment with valve seat | contact maintenance and the machine shop to correct this problem and replace the valve
163 | 46 | mechanical | valves | hand-operated valve difficult to open | gland packing too tight | slacken off the gland follower, and allow the packing to move slightly
164 | 46 | mechanical | valves | hand-operated valve difficult to open | gland packing badly installed | repack the valve
165 | 47 | mechanical | chain drives | noisy drive | incorrect tension | check the slack side span for 2% deflection, and adjust the chain tension as necessary
166 | 47 | mechanical | chain drives | noisy drive | insufficient lubrication | check the drive for proper lubrication. lubricate the drive as necessary
167 | 47 | mechanical | chain drives | noisy drive | worn drive | check the chain and sprocket for wear, and have it replaced if worn
168 | 47 | mechanical | chain drives | noisy drive | misalignment of sprockets | check the alignment, and realign as necessary
169 | 47 | mechanical | chain drives | noisy drive | loose casing or bearings | draw up all bolts and brace the casings as required
170 | 47 | mechanical | chain drives | noisy drive | pitch too large | check chain drive spec chart. change the chain
171 | 48 | mechanical | chain drives | chain climbing sprocket teeth | chain worn | check for chain wear. replace chain as necessary
172 | 48 | mechanical | chain drives | chain climbing sprocket teeth | insufficient tension | check chain tension. increase tension as needed
173 | 48 | mechanical | chain drives | chain climbing sprocket teeth | material in tooth pockets | clean sprocket. eliminate cause of material buildup
174 | 48 | mechanical | chain drives | chain climbing sprocket teeth | chains & sprockets fit poorly | notify the maintenance department
175 | 48 | mechanical | chain drives | chain climbing sprocket teeth | insufficient chain wrap | change the driver arrangement to get more sprocket-teeth in contact with the chain, or use an idler take-up sprocket to increase the wrap
176 | 48 | mechanical | chain drives | chain climbing sprocket teeth | excessive chain slack | adjust the centers or take-up sprockets for a 2% final deflection
177 | 49 | mechanical | chain drives | drive is running excessively hot | running too fast | check drive for proper speed. adjust as required
178 | 49 | mechanical | chain drives | drive is running excessively hot | insufficient lubrication | check for the correct type and amount of lubricant
179 | 49 | mechanical | chain drives | drive is running excessively hot | chain operating too fast for bath lubrication | use the oil stream system to lubricate the chain
180 | 49 | mechanical | chain drives | drive is running excessively hot | chain immersed too deeply in oil bath in bath-lubricated drive | check the drive for obstructions, and check the guard design. remove all obstructions
181 | 50 | mechanical | chain drives | chain hanging in sprocket | worn sprocket teeth | check for chain wear and replace the chain as necessary
182 | 50 | mechanical | chain drives | chain hanging in sprocket | material buildup on driver sprocket tooth pockets | clean and lubricate the sprockets correctly
183 | 50 | mechanical | chain drives | chain hanging in sprocket | sticky lubricant | check the grade of the lubricant, and refer to the lubricant chart for that particular chain drive configuration. replace with the recommended lubricant as necessary
184 | 51 | mechanical | chain drives | chain whip | insufficient tension | correct the tension. the tension should be set to deflect 2% of the pitch between the driver and the driven sprockets
185 | 51 | mechanical | chain drives | chain whip | stiff chain joints | replace the bad joints or install a new chain
186 | 51 | mechanical | chain drives | chain whip | excessive chain slack | install a chain take-up or idler sprocket or adjust the centers of the sprockets
187 | 51 | mechanical | chain drives | chain whip | high pulsating loads | reduce the load where possible or replace the chain with one of suitable length
188 | 51 | mechanical | chain drives | chain whip | nonuniform chain wear | investigate why the chain is wearing in an irregular manner. replace the chain
189 | 52 | mechanical | chain drives | stiff chain joints | misalignment of drive | have maintenance check the alignment and correct as necessary
190 | 52 | mechanical | chain drives | stiff chain joints | worn and corroded chain | replace the chain. provide the correct lubrication
191 | 52 | mechanical | chain drives | stiff chain joints | inadequate lubrication | clean and lubricate the chain correctly. refer to the lube manual for the correct lubricant and application
192 | 52 | mechanical | chain drives | stiff chain joints | corrosion on the chain | remove any corrosion, lubricate the chain correctly, and protect the chain from further corrosion by keeping it clean and well lubricated
193 | 52 | mechanical | chain drives | stiff chain joints | excessive overload | identify the overload cause and reduce it
194 | 52 | mechanical | chain drives | stiff chain joints | material buildup in joints | clean and lubricate the chain more frequently
195 | 52 | mechanical | chain drives | stiff chain joints | peening edges of side plate metal | check for chain interference and repair as necessary to remove peeping marks
196 | 53 | mechanical | chain drives | wear on chain link plates or sides of sprocket teeth | misalignment of the drive chain | remove the chain and correct the alignment of the sprockets and shafts
197 | 53 | mechanical | chain drives | broken pins, bushings, or rollers | chain speed too high for the pitch and sprocket size | check the number of sprocket teeth to ensure that it is within the recommended limits for the speed involved. use a shorter pitch chain of equal or greater strength. select a sprocket with more teeth, if necessary
198 | 53 | mechanical | chain drives | broken pins, bushings, or rollers | material buildup in sprocket tooth pockets | remove material buildup from the sprockets
199 | 53 | mechanical | chain drives | broken pins, bushings, or rollers | heavy shock or suddenly applied loads | reduce the shock loads
200 | 54 | mechanical | chain drives | broken pins, bushings, or rollers (continued) | nan | check the shaft runout for eccentricity paying particular attention to the locking device on the sprocket hub. the locking device can draw the hub off-center if there is a loose fit on the shaft
201 | 54 | mechanical | chain drives | broken pins, bushings, or rollers (continued) | inadequate lubrication | lubricate the chain correctly
202 | 54 | mechanical | chain drives | broken pins, bushings, or rollers (continued) | poorly fitted sprockets | check the sprockets for wear and correct the bottom diameter
203 | 54 | mechanical | chain drives | broken pins, bushings, or rollers (continued) | chain or sprocket corrosion | remove any corrosion from the chain or sprocket, lubricate the chain correctly, and protect the chain and sprocket from further corrosion by keeping the chain clean and well lubricated
204 | 55 | mechanical | chain drives | pulsation | chain tension too low | adjust the take-ups to restore the proper tension
205 | 55 | mechanical | chain drives | pulsation | chain speed too slow | increase the size of the sprocket or increase the conveyor speed
206 | 55 | mechanical | chain drives | pulsation | obstruction | remove the obstruction and ensure that the lower strand is not striking a foreign object
207 | 55 | mechanical | chain drives | pulsation | heavy or tacky lubricants | clean and lubricate the chain correctly
208 | 55 | mechanical | chain drives | pulsation | sprockets with too few teeth, causing a large amount of chordal action | replace with sprockets having the correct number of teeth
209 | 55 | mechanical | chain drives | pulsation | eccentricity | correct eccentricity of hub hole
210 | 56 | mechanical | chain drives | broken sprocket teeth | obstruction striking the cotter pins | check the chain and sprocket clearances. remove any foreign materials
211 | 56 | mechanical | chain drives | broken sprocket teeth | excessive shock loads, especially with small, cast-iron sprockets | reduce excessive shock loads or change to steel sprockets
212 | 56 | mechanical | chain drives | cotter pins coming out | obstructions striking the cotter pins | eliminate the obstruction. tap the ends back until the cotter pin fits snugly against the side plates or use a riveted chain
213 | 56 | mechanical | chain drives | cotter pins coming out | cotter pins not installed properly, not spread apart and drawn back snugly against the side plates | correct the faulty installation
214 | 57 | mechanical | chain drives | damaged conveyed articles | bent or damaged flights, attachments, or links | repair or replace the damaged parts
215 | 57 | mechanical | chain drives | damaged conveyed articles | obstruction in throughways or casings | remove the obstruction
216 | 57 | mechanical | chain drives | damaged conveyed articles | improper timing | check timing sequence, chain elongation, and chain selection
217 | 58 | mechanical | gear boxes | noisy operation of the unit | misalignment | check the alignment of the unit. check the condition of the coupling. if misalignment is the problem, have the maintenance group perform an alignment of the shafts
218 | 58 | mechanical | gear boxes | noisy operation of the unit | faulty lubrication | check oil level. add lubricant if needed. determine if lubricant is the correct grade. if the lubricant is not the correct grade, replace with the correct lubricant
219 | 58 | mechanical | gear boxes | noisy operation of the unit | excessive tension on the belts or the chain | check the tension and alignment of the drive auxiliaries and relieve the tension if required
220 | 58 | mechanical | gear boxes | noisy operation of the unit | worn parts | adjust or replace the worn parts
221 | 58 | mechanical | gear boxes | noisy operation of the unit | overloading | reduce the load
222 | 59 | mechanical | gear boxes | excessive operating temperature | incorrect lubricant | check the lubricant against the specification instructions. replace with the correct lubricant
223 | 59 | mechanical | gear boxes | excessive operating temperature | incorrect amount of lubricant | check the level in the sight glass, and fill to the correct level. ensure that the air breather is clean and functioning properly
224 | 59 | mechanical | gear boxes | excessive operating temperature | overloading | reduce the load
225 | 59 | mechanical | gear boxes | excessive operating temperature | obstructed air flow | check the air supply for proper fan circulation. remove any obstructions. avoid any high surrounding ambient temperatures. if the ambient temperature is high because of a local heat source, place some form of barrier between the heat source and the machine
226 | 60 | mechanical | gear boxes | oil leakage | too much oil in the unit | recheck the oil level with the unit shut down. remove any excess oil
227 | 60 | mechanical | gear boxes | oil leakage | clogged air breather | remove the breather, and clean it
228 | 60 | mechanical | gear boxes | oil leakage | loose bolts and nuts in jointed areas | tighten all of the joints and end cap bolts
229 | 60 | mechanical | gear boxes | loosened mounting bolts | vibration from fluctuating loads or misalignment | check and realign the system. tighten all of the bolts
230 | 61 | mechanical | Lubricating Oil Systems | system pressure too low | open drain-back valve from pressure line to return line | close the pump relief valves
231 | 61 | mechanical | Lubricating Oil Systems | system pressure too low | pump relief valve or system pressure control valve set low | check pump relief valves and the pressure control valve for normal operation. adjust as needed
232 | 61 | mechanical | Lubricating Oil Systems | system pressure too low | oil leak(s) in the system | check for an oil leak. repair as necessary
233 | 61 | mechanical | Lubricating Oil Systems | system pressure too high | system pressure control valve set too high or not functioning properly | check the system control valve, and adjust as needed
234 | 61 | mechanical | Lubricating Oil Systems | system pressure too high | plugged flow nozzle(s) | check the flow controls for proper settings and positive indication of flow. adjust the setting as necessary
235 | 62 | mechanical | Lubricating Oil Systems | system pressure constantly fluctuating | system pressure control valve not functioning properly | adjust the system pressure control valve to maintain a constant system pressure
236 | 63 | mechanical | Lubricating Oil Systems | very erratic pressures and sight flows, indicating a very uneven and bumpy flow | air being drawn into the system and pumped with the oil | check the oil level in the reservoir and the free-floating operation of the floating suction. verify there are no obstructions causing flowing suction to stick. remove any debris from operation area. check the suction line and the strainer to the pump for a possible air leak. check the pressure tanks. if the tank is empty of oil, air may be leaking into the system from the air connection. add oil as necessary
237 | 63 | mechanical | Lubricating Oil Systems | sounding of alarm | dirty filter | purge any air from the filter casing before changing over to the standby filter to put it into service
238 | 63 | mechanical | Lubricating Oil Systems | sounding of alarm | high differential pressure across the filter | purge any air from the filter casing before changing over to the standby filter to put it into service
239 | 64 | mechanical | Lubricating Oil Systems | standby pump and alarm cycling on and off | operating pump not running | change the pump selector switch to reverse pumps. if the system now runs normally, investigate the pump taken out of service for a problem, such as a broken shaft
240 | 64 | mechanical | Lubricating Oil Systems | standby pump and alarm cycling on and off | mercoid switches incorrectly set | set the standby mercoid switch approximately 5 and 15 psi below the desired system pressure
241 | 64 | mechanical | Lubricating Oil Systems | standby pump and alarm cycling on and off | increased demand for oil from the system due to an oil leak | look for oil leaks or some drastic change causing increased oil flow
242 | 64 | mechanical | Lubricating Oil Systems | standby pump and alarm cycling on and off | oil temperature too high | check that oil temperature on discharge side of cooler is within 10 °f of operational temperature. if it is not, make adjustments accordingly
243 | 65 | mechanical | Lubricating Oil Systems | pump running noisily | low fluid level | adjust the fluid supply to the pump
244 | 65 | mechanical | Lubricating Oil Systems | pump running noisily | system pressure too high | adjust the pressure-relief valve to lower the pressure
245 | 65 | mechanical | Lubricating Oil Systems | pump running noisily | variable-volume or pressure-compensated pump adjusted for too much flow | adjust the pump
246 | 65 | mechanical | Lubricating Oil Systems | pump running noisily | intake leaking | locate and correct the leak
247 | 65 | mechanical | Lubricating Oil Systems | pump running noisily | pump speed too high | decrease the pump speed
248 | 65 | mechanical | Lubricating Oil Systems | pump running noisily | motor and pump not aligned | have maintenance align the motor and pump
249 | 65 | mechanical | Lubricating Oil Systems | pump running noisily | restricted intake | find obstruction. clear intake. clean suction filters
250 | 65 | mechanical | Lubricating Oil Systems | pump running noisily | worn pump | repair or replace the pump
251 | 66 | mechanical | Lubricating Oil Systems | pump running noisily (continued) | cavitation caused by lack of net positive suction head (npsh) or turbulence from sharp pipe bends immediately upstream of the pump suction | lower the suction temperature
252 | 66 | mechanical | Lubricating Oil Systems | pump running noisily (continued) | suction pressure lower than the corresponding saturation temperature | lower the suction temperature
253 | 66 | mechanical | Lubricating Oil Systems | pump running noisily (continued) | recirculation of fluid at the impeller vane exit area | avoid discharge restrictions. increase the clearance at exit tips of vanes. /never/ install higher horsepower driver without redesigning discharge and suction piping
254 | 67 | mechanical | V-Belt Drives | belt slipping | not enough tension | increase the tension. the deflection of the belt at midspan should be 1/64' for each inch of span between the centerlines of the driven and driving sheaves
255 | 67 | mechanical | V-Belt Drives | belt slipping | drive overloaded | increase the belt size
256 | 67 | mechanical | V-Belt Drives | belt slipping | contaminants on belts or sheaves | clean or change the belts or sheaves
257 | 67 | mechanical | V-Belt Drives | belt slipping | heavy starting load | increase the tension
258 | 67 | mechanical | V-Belt Drives | belt slipping | not enough arc of contact | lengthen the center distance, or use an idler
259 | 68 | mechanical | V-Belt Drives | belt turned over in sheave | broken cords from prying belts on and off sheaves | reduce the drive centers when you are installing the belts. adjust the motor position to lessen the tension on the belts. install new belts, and retention them
260 | 68 | mechanical | V-Belt Drives | belt turned over in sheave | not enough tension | increase the tension
261 | 69 | mechanical | V-Belt Drives | repeated belt breakage | shock loads | test the shaft runout for eccentricity. have maintenance make repairs. increase the tension or drive capacity
262 | 69 | mechanical | V-Belt Drives | repeated belt breakage | broken cords from running or prying belts on and off sheaves | reduce the drive centers when you are installing the belts. adjust the motor position to lessen the tension on the belts. install new belts, and retention them
263 | 69 | mechanical | V-Belt Drives | repeated belt breakage | foreign objects falling into the sheaves | provide protective guards
264 | 70 | mechanical | V-Belt Drives | rapid wear of the belt | worn sheave grooves | replace the sheaves
265 | 70 | mechanical | V-Belt Drives | rapid wear of the belt | sheave diameter too small | increase the sheave diameter
266 | 70 | mechanical | V-Belt Drives | rapid wear of the belt | misalignment | align the drive
267 | 70 | mechanical | V-Belt Drives | rapid wear of the belt | drive overloaded | increase the drive capacity
268 | 70 | mechanical | V-Belt Drives | rapid wear of the belt | belts rubbing | provide the correct running clearance
269 | 70 | mechanical | V-Belt Drives | rapid wear of the belt | contaminated environment | clean and protect the belts
270 | 71 | mechanical | V-Belt Drives | belt cracked and hardened, causing slippage | excessive heat | track down and eliminate the heat source. provide ventilation
271 | 71 | mechanical | V-Belt Drives | belt whipping | drive centers too long | reduce the drive centers, or provide an idler
272 | 71 | mechanical | V-Belt Drives | belt whipping | tensioner idler sheave out of adjustment | reduce the drive centers, or provide an idler
273 | 71 | mechanical | V-Belt Drives | hot bearings | inadequate bearing lubrication | lubricate the bearing
274 | 71 | mechanical | V-Belt Drives | hot bearings | too much bearing lubricant | open the vent/drain plug, and purge the lubricant cavity with fresh lubricant. leave the vent open for approximately 30 minutes, and then close it
275 | 72 | mechanical | V-Belt Drives | hot bearings (continued) | drive belts too tight | adjust the belt tension. the deflection of the belt at midspan should be 1/64' for each inch of span between the centerlines of the driven and driving sheaves
276 | 73 | mechanical | V-Belt Drives | one or two belts broken in a set | not a matched set of drive belts | replace the drive belts with matching belts
277 | 73 | mechanical | V-Belt Drives | one or two belts broken in a set | belts broken internally because of poor installation practices | move the motor inwards to detension the belts, and replace with matching belts, using the proper installation procedure. /caution/ do not use different manufacturers' belts to make up a set. always use belts from one manufacturer because manufacturing processes differ from one manufacturer to another
278 | 74 | mechanical | V-Belt Drives | excessive belt stretch | improper amount of take-up since the initial belt installation | replace all the belts
279 | 74 | mechanical | V-Belt Drives | excessive belt stretch | overload on the drive belt | reduce the overload, or install a larger drive system
280 | 74 | mechanical | V-Belt Drives | excessive belt stretch | internal breaks in the belt | replace the belt. /caution/ never use a pry bar to install the belt in the sheave because this breaks the inner fibers on the belt and can break the sidewalls of the sheave
281 | 75 | mechanical | V-Belt Drives | unequal belt stretch | not a matching set of belts | replace with matching belts
282 | 75 | mechanical | V-Belt Drives | unequal belt stretch | unequal coefficient of friction | check and adjust the alignment of the sheaves, and correct the tension
283 | 75 | mechanical | V-Belt Drives | unequal belt stretch | nonparallel shafts | check and adjust the alignment of the sheaves, and correct the tension
284 | 75 | mechanical | V-Belt Drives | unequal belt stretch | internal and non-visible breaks in belts | replace the belts
285 | 75 | mechanical | V-Belt Drives | unequal belt stretch | broken belt cords | replace the belts
286 | 75 | mechanical | V-Belt Drives | unequal belt stretch | worn grooves in sheaves | replace the sheaves
287 | 76 | mechanical | V-Belt Drives | belt separation | small sheaves | replace with properly sized sheaves
288 | 76 | mechanical | V-Belt Drives | belt separation | excessive belt tension | check and adjust the belt tension
289 | 76 | mechanical | V-Belt Drives | topside belt wear | belt obstruction | remove the obstruction
290 | 76 | mechanical | V-Belt Drives | topside belt wear | turned over or twisted belt | adjust and inspect the belt. replace as required
291 | 76 | mechanical | V-Belt Drives | opening of the envelope seam on belt | rubber solvent or oil on the belt | clean and inspect the belt. replace the belt as required
292 | 77 | mechanical | V-Belt Drives | abnormal envelope wear | abrasive condition | check the belt for an abrasive condition or any of the conditions mentioned as a probable cause; replace the belts as required
293 | 77 | mechanical | V-Belt Drives | abnormal envelope wear | worn sheaves | check the belt for an abrasive condition or any of the conditions mentioned as a probable cause; replace the belts as required
294 | 77 | mechanical | V-Belt Drives | abnormal envelope wear | improper sheave angle | check the belt for an abrasive condition or any of the conditions mentioned as a probable cause; replace the belts as required
295 | 77 | mechanical | V-Belt Drives | abnormal envelope wear | slip | check the belt for an abrasive condition or any of the conditions mentioned as a probable cause; replace the belts as required
296 | 77 | mechanical | V-Belt Drives | abnormal envelope wear | exposed to chemical fumes | check the belt for an abrasive condition or any of the conditions mentioned as a probable cause; replace the belts as required
297 | 77 | mechanical | V-Belt Drives | abnormal envelope wear | obstructions | check the belt for an abrasive condition or any of the conditions mentioned as a probable cause; replace the belts as required
298 | 77 | mechanical | V-Belt Drives | abnormal envelope wear | high heat | check the belt for an abrasive condition or any of the conditions mentioned as a probable cause; replace the belts as required
299 | 77 | mechanical | V-Belt Drives | belt soft or swollen | rubber solvent or oil on the belt | clean and inspect the belt; replace the belt as required
300 | 77 | mechanical | V-Belt Drives | belt envelope hardening and cracking | exposure to severe heat and/or chemical fumes | clean and inspect the belt; replace the belt as required
301 | 78 | mechanical | Fan Systems | fan output below scfm | total resistance on system higher than expected | check whether any other fans are discharging into the same outlet as the fan having problems; this could be a design problem; inform engineering for an evaluation
302 | 78 | mechanical | Fan Systems | fan output below scfm | dampers closed or partially closed | check to see whether any dampers have been accidentally closed; open any dampers that should be open
303 | 78 | mechanical | Fan Systems | fan output below scfm | speed too slow | check the drive belts for slippage. adjust the tension if the belts are not damaged. ensure there is adequate lubrication to bearings. have the electricians check out the motor
304 | 79 | mechanical | Fan Systems | fan output below scfm (continued) | dampers or variable inlet vanes incorrectly set | readjust the damper control linkage turnbuckles to the calibrated setpoints
305 | 79 | mechanical | Fan Systems | fan output below scfm (continued) | poor fan inlet conditions, such as choked filters | check the pressure differential across the filters, and clean or replace the dirty filters
306 | 79 | mechanical | Fan Systems | fan output below scfm (continued) | atmospheric air induction through ducting leaks | walk ducting system down, and check for leaks. an ultrasonic leak detector is an ideal tool to determine exactly where leaks occur
307 | 79 | mechanical | Fan Systems | fan output below scfm (continued) | fan rotation wrong | ensure that the belt drive is not crossed. have the electricians check the rotation of the motor
308 | 79 | mechanical | Fan Systems | fan output below scfm (continued) | wheel mounted backward on the shaft | stop the fan, and have maintenance reverse the wheel
309 | 80 | mechanical | Fan Systems | vibration and noise | unbalance due to dirt buildup on fan blades | perform vibration analysis to determine the magnitude of the problem, and then balance the fan. water wash the fan blades to remove the buildup of dirt. if the fan operates in a boiler exhaust system or some other high-temperature gaseous system, descale the blades
310 | 80 | mechanical | Fan Systems | vibration and noise | poor foundations or warped baseplate | check the foundations for cracks and breakage. report the findings to engineering for resolution
311 | 81 | mechanical | Fan Systems | vibration and noise (continued) | misalignment | perform vibration analysis to determine the magnitude of the problem, and then align the fan shafts
312 | 81 | mechanical | Fan Systems | vibration and noise (continued) | soft-foot conditions | perform a soft-foot check on all the feet of the unit to determine if a soft-foot condition is the problem. add or remove shims to correct condition
313 | 81 | mechanical | Fan Systems | vibration and noise (continued) | no zero cold-spring of ductwork at the fan connection | check for ducting distortion if no expansion or flex joint is fitted. adjust the hangers as needed
314 | 82 | mechanical | Fan Systems | damaged bearings | belt drive misalignment | ensure that the sheaves are the same width and are properly aligned with each other
315 | 82 | mechanical | Fan Systems | damaged bearings | bad lubrication | ensure that the correct lubricant is being used and that the bearings are vented during the lubricant application
316 | 83 | mechanical | Fan Systems | damaged bearings (continued) | nan | ensure that the bearing installation practices are correct
317 | 83 | mechanical | Fan Systems | damaged bearings (continued) | nan | when the fan is off, ensure that the unit is turned to change the resting point periodically to prevent the shaft from sagging due to its own weight. check the bearing mounts for undue stress due to bad foundations and misaligned ductwork
318 | 84 | mechanical | Fan Systems | damaged bearings (continued) | misaligned belt drives | ensure that the belts are sitting in the correct sheaves and are aligned to run true in the v-grooves. check the lineup of the sidewalls of the sheaves with a straightedge or a stretched string
319 | 85 | mechanical | Fan Systems | damaged bearings (continued) | worn coupling | conduct a vibration analysis to determine whether the coupling is worn. the wrong grade of lubricant may have been used and accumulated in one spot, causing an unbalanced condition
320 | 85 | mechanical | Fan Systems | damaged bearings (continued) | resonance effect from another machine(s) | perform an evaluation to determine the extent of resonance and to track down the excitation source(s). to temporarily stop resonance-induced vibration, alter the mass of the unit by placing some weight, such as a bag of sand, on the unit
321 | 85 | mechanical | Fan Systems | damaged bearings (continued) | fan rotating in the wrong direction | have electricians check the motor rotation and correct the rotation as required
322 | 86 | mechanical | Fan Systems | damaged bearings (continued) | partial offset restriction on inlet side of fan, causing it to unload | ensure that no foreign objects are causing a partial blockage on the inlet side of the fan. as fan blades turn past the obstruction, they will be unable to carry the full load and deflect
323 | 86 | mechanical | Fan Systems | bearing overheating | overlubrication of bearing | determine the capacity of the bearing and follow the manufacturer's recommendations for lubrication
324 | 86 | mechanical | Fan Systems | bearing overheating | misalignment | ensure that the belts are sitting in the correct sheaves and are aligned to run true in the v-grooves. check the lineup of the sidewalls of the sheaves with a straightedge or a stretched string
325 | 87 | mechanical | Fan Systems | bearings overheating (continued) | unbalance | rotate the shaft, and let it roll until it comes to rest on its own to check for static unbalance. static unbalance can be corrected by hanging an appropriate weight opposite the resting, 6 o'clock position. engineers who have the proper instrumentation should do more complex balance correction
326 | 87 | mechanical | Fan Systems | bearings overheating (continued) | bent shaft | when the fan is off, make sure the unit is turned off the resting point periodically to prevent the shaft from sagging due to its owm weight. check for undue stress on bearing mounts because of bad foundations and misaligned ductwork
327 | 88 | mechanical | Fan Systems | bearings overheating (continued) | over-tensioned belts | depress the belts at midspan, and measure the deflection to test the belt tension. the deflection should be equal to 1/64' per inch of span between the centers of the driven and driver units
328 | 88 | mechanical | Fan Systems | bearings overheating (continued) | abnormal axial thrusting caused by misaligned belts | this can be caused by gross misalignment between the driver and the driven units. it can also be caused when one sheave is wider than the other one. to correct either one, align the belts to the center of the v in each sheave
329 | 89 | mechanical | Fan Systems | bearings overheating (continued) | sheaves that have eccentric bores due to poor machining practices or cast with boss off-center | plug the bore, and remachine it true. eccentric bores cause the sheaves to turn off center, causing the belts to tension and detension each revolution. this continual jerking back and forth causes the bearings to take a terrible pounding. keys and setscrews can have the same effect by drawing a sheave ofllcenter when the force is tightened
330 | 90 | mechanical | Steam Traps | trap blowing live steam | no prime, bucket, or traps because trap not primed when originally installed | prime the trap
331 | 90 | mechanical | Steam Traps | trap blowing live steam | no prime, bucket, or traps because trap not primed after cleaned | prime the cleaned trap
332 | 91 | mechanical | Steam Traps | trap blowing live steam (continued) | bypass valve open or leaking | remove or repair the bypass valve
333 | 91 | mechanical | Steam Traps | trap blowing live steam (continued) | sudden pressure drop | install a check valve ahead of the trap
334 | 92 | mechanical | Steam Traps | trap blowing live steam (continued) | valve mechanism not closing because scale or dirt lodged in orifice | clean the trap
335 | 92 | mechanical | Steam Traps | trap blowing live steam (continued) | worn or defective valve or disc mechanism | repair or replace the defective parts
336 | 92 | mechanical | Steam Traps | trap blowing live steam (continued) | ruptured bellows (thermostatic traps) | replace the bellows
337 | 93 | mechanical | Steam Traps | trap blowing live steam (continued) | back pressure too high in a thermodynamic trap because worn or defective parts | repair or replace the defective parts
338 | 93 | mechanical | Steam Traps | trap blowing live steam (continued) | back pressure too high in a thermodynamic trap because trap stuck open | clean the trap
339 | 93 | mechanical | Steam Traps | trap blowing live steam (continued) | back pressure too high in a thermodynamic trap because undersized condensate return line or pig tank | increase the line or pig tank size
340 | 93 | mechanical | Steam Traps | trap blowing live steam (continued) | back pressure too high in a thermodynamic trap because blowing flash steam caused by flash steam forming when the condensate is released to a lower or atmospheric pressure | no corrective action is required for this normal condition
341 | 94 | mechanical | Steam Traps | trap not discharging | pressure too high because trap rating too low | install the correct size trap
342 | 94 | mechanical | Steam Traps | trap not discharging | pressure too high because orifice enlarged by normal wear | replace the worn orifice
343 | 94 | mechanical | Steam Traps | trap not discharging | pressure too high because pressure-reducing valve set too high or broken | readjust or replace the pressure-reducing valve. the valve may require a new diaphragm
344 | 94 | mechanical | Steam Traps | trap not discharging | pressure too high because system pressure raised | install the correct pressure change assembly
345 | 95 | mechanical | Steam Traps | trap not discharging (continued) | condensate not reaching the trap because strainer clogged | blow out the screen with air, or replace it
346 | 95 | mechanical | Steam Traps | trap not discharging (continued) | condensate not reaching the trap because obstruction in the line to the trap | remove the obstruction
347 | 95 | mechanical | Steam Traps | trap not discharging (continued) | condensate not reaching the trap because bypass valve opening or leaking | remove or repair the bypass valve
348 | 96 | mechanical | Steam Traps | trap not discharging (continued) | condensate not reaching the trap because steam supply line shut off | open the steam supply valve
349 | 96 | mechanical | Steam Traps | trap not discharging (continued) | condensate not reaching the trap because trap clogged with foreign matter | clean the strainer, and reinstall it
350 | 96 | mechanical | Steam Traps | trap not discharging (continued) | condensate not reaching the trap because trap held closed by a defective mechanism | repair or replace the defective mechanism
351 | 96 | mechanical | Steam Traps | trap not discharging (continued) | condensate not reaching the trap because high vacuum in the condensate return line | install the correct pressure change assembly
352 | 97 | mechanical | Steam Traps | trap not discharging (continued) | no pressure differential across the trap because blocked or restricted condensate return line | remove the restriction
353 | 97 | mechanical | Steam Traps | trap not discharging (continued) | no pressure differential across the trap because incorrect pressure change assembly | install the correct pressure change assembly
354 | 98 | mechanical | Steam Traps | continuous discharge from trap | trap too small and undersized for the capacity being handled | install the proper size trap
355 | 98 | mechanical | Steam Traps | continuous discharge from trap | trap pressure rating too high | install the correct pressure change assembly
356 | 98 | mechanical | Steam Traps | continuous discharge from trap | trap clogged | clean the trap internals, and reinstall the strainer
357 | 98 | mechanical | Steam Traps | continuous discharge from trap | strainer plugged | clean the strainer
358 | 98 | mechanical | Steam Traps | continuous discharge from trap | bellows overstressed in a thermostatic trap | replace the bellows
359 | 99 | mechanical | Steam Traps | continuous discharge from trap | loss of the prime | install a check valve on the inlet side of the trap
360 | 98 | mechanical | Steam Traps | continuous discharge from trap | failure of valve to seat due to worn valve and seat | replace the worn parts
361 | 99 | mechanical | Steam Traps | continuous discharge from trap (continued) | scale and dirt deposits under the valve and in the orifice | clean the trap
362 | 99 | mechanical | Steam Traps | continuous discharge from trap (continued) | worn guide pins and lever | replace the worn parts
363 | 99 | mechanical | Steam Traps | sluggish or uneven heating | capacity margin in trap for heavy starting loads | install the proper size larger trap
364 | 99 | mechanical | Steam Traps | sluggish or uneven heating | insufficient air handling capacity on bucket traps | use thermic buckets, or increase the vent size
365 | 99 | mechanical | Steam Traps | sluggish or uneven heating | short circuiting by using group traps | when steam traps are grouped, i.e. multiple traps are run into the same line, there is a possibility of condensate backup due to pressure inconsistencies or obstructions. systems with many traps feeding into one return line are hard to troubleshoot because it is hard to determine which trap has the problem. pipe traps individually from vessels
366 | 100 | mechanical | Steam Traps | sluggish or uneven heating (continued) | inadequate steam supply due to pressure valve change | restore normal steam pressure
367 | 100 | mechanical | Steam Traps | sluggish or uneven heating (continued) | steam pressure-reducing valve setting off | readjust or replace the reducing valve
368 | 100 | mechanical | Steam Traps | back pressure troubles | condensate return line too small | install a larger condensate return line
369 | 100 | mechanical | Steam Traps | back pressure troubles | other traps blowing steam into header | locate and repair other faulty traps
370 | 100 | mechanical | Steam Traps | back pressure troubles | pig tank vent line plugged | clean out pig tank vent line
371 | 100 | mechanical | Steam Traps | back pressure troubles | obstruction in return line | remove the obstruction
372 | 100 | mechanical | Steam Traps | back pressure troubles | excess vacuum in return line | install the correct pressure change assembly
373 | 101 | electrical | Electric Motors | motor not starting | blown fuses | replace with fuses that are at least 12% of the amperes listed on the nameplate
374 | 101 | electrical | Electric Motors | motor not starting | overload trips | check and reset the overload in the starter
375 | 101 | electrical | Electric Motors | motor not starting | improper current supply | verify that the current supplied matches the specifications on the motor nameplate and the load factor
376 | 101 | electrical | Electric Motors | motor not starting | improper line connections | check the connections, using the diagram supplied with the motor. if the wiring is connected improperly, have the electricians rewire it to the connection specified on the diagram
377 | 102 | electrical | Electric Motors | motor not starting (continued) | open circuit in the winding or the starting switch | have an electrician check for loose wiring connections. verify that the starting switch inside the motor is closed. note: a humming sound when the switch is closed indicates an open circuit. repulsion induction motors may spark at the brushes
378 | 102 | electrical | Electric Motors | motor not starting (continued) | mechanical failure | stop the motor, and ensure that the motor and drive turn freely. check the bearings and lubrication. add some lubricant to the bearings, and rotate the shaft slowly by hand. if it still feels rough, have the motor repaired by the maintenance group
379 | 103 | electrical | Electric Motors | motor not starting (continued) | short-circuited stator | have maintenance rewind the motor. note: blown fuses indicate short-circuited stator
380 | 103 | electrical | Electric Motors | motor not starting (continued) | poor stator coil connection | remove the end bell, and locate the connection problem, using a test lamp. if a fault is found, have the electricians repair it
381 | 103 | electrical | Electric Motors | motor not starting (continued) | defective rotor | look for broken bars or end ring, replace/repair
382 | 103 | electrical | Electric Motors | motor not starting (continued) | overloaded motor | reduce the load
383 | 103 | electrical | Electric Motors | motor not starting (continued) | one phase of three-phase motor open | check the lines for the open phase
384 | 103 | electrical | Electric Motors | motor not starting (continued) | short-circuited stator | have maintenance rewind the motor. note: blown fuses indicate short-circuited stator
385 | 104 | electrical | Electric Motors | motor not starting (continued) | worn or sticking brushes on repulsion induction motors | check for wear, and replace as necessary. check for the correct brush pressure. clean the commutator if it is dirty
386 | 104 | electrical | Electric Motors | motor stalling | wrong application | verify that the type or size of motor is correct and is within the specified operational parameters. if the motor is not correct, an electrician should install a new motor that meets the specifications
387 | 104 | electrical | Electric Motors | motor stalling | overloaded motor | reduce the load
388 | 104 | electrical | Electric Motors | motor stalling | low motor voltage | ensure the nameplate voltage is restored and maintained
389 | 104 | electrical | Electric Motors | motor stalling | open circuit due to blown fuses | check overload relay, stator, and the push buttons to reset the fuses. replace the fuses if necessary
390 | 105 | electrical | Electric Motors | motor stalling (continued) | incorrect control resistance of wound motor | check the control sequence replace the broken resistors. repair the open circuits
391 | 105 | electrical | Electric Motors | motor running and then dying down | power failure | have an electrician check for loose connections to the line, to the fuses, and to the control. correctly tighten any loose connections that are found
392 | 105 | electrical | Electric Motors | motor not coming up to speed | motor not properly sized for designed load of the system | consult supplier for the proper type of motor, and replace the motor with the correctly sized unit
393 | 105 | electrical | Electric Motors | motor not coming up to speed | voltage too low at motor terminals due to line drop | use a higher voltage on the transformer terminals, or reduce the load
394 | 105 | electrical | Electric Motors | motor not coming up to speed | improper control operation of the secondary resistance of the wound motor | correct the secondary control
395 | 106 | electrical | Electric Motors | motor not coming up to speed (continued) | starting load too high | check the load that the motor is supposed to carry at the start, and adjust as necessary
396 | 106 | electrical | Electric Motors | motor not coming up to speed (continued) | broken rotor bars | look for cracks near the rings, and repair or replace as necessary. new rotor may be needed. repairs are usually temporary
397 | 106 | electrical | Electric Motors | motor not coming up to speed (continued) | open primary circuit | locate the fault, using a resting device
398 | 106 | electrical | Electric Motors | motor taking too long to accelerate | excess loading | reduce the load
399 | 106 | electrical | Electric Motors | motor taking too long to accelerate | poor circuit | check for high resistance. have an electrician correct any deficiencies found. refer to the manufacturer's manual for guidance
400 | 106 | electrical | Electric Motors | motor taking too long to accelerate | defective squirrel-cage rotor | replace with a new rotor
401 | 107 | electrical | Electric Motors | motor taking too long to accelerate (continued) | applied voltage too low | have the power company increase the power tap
402 | 107 | electrical | Electric Motors | wrong rotation | wrong sequence of phases | reverse connections at motor or switchboard
403 | 107 | electrical | Electric Motors | motor overheating while running under load | overload | reduce the load
404 | 107 | electrical | Electric Motors | motor overheating while running under load | wrong blowers or air shields that may be clogged with dirt, preventing the proper ventilation of the motor | clean the blower or air shield. note: a continuous stream of air leaving the motor indicates good ventilation. if this does not happen after cleaning, check with the manufacturer for advice. if the wrong blower or air shield is being used, the manufacturer may have to recommend a design change
405 | 107 | electrical | Electric Motors | motor overheating while running under load | one phase of motor open | ensure that all of the leads are well connected
406 | 108 | electrical | Electric Motors | motor overheating while running under load (continued) | grounded coil | locate the fault and repair
407 | 108 | electrical | Electric Motors | motor overheating while running under load (continued) | unbalanced terminal voltage | check for faulty leads, connections, and transformers. and repair or replace as necessary
408 | 108 | electrical | Electric Motors | motor overheating while running under load (continued) | shorted stator coil | repair, and then check the wattmeter reading
409 | 108 | electrical | Electric Motors | motor overheating while running under load (continued) | high resistance | have an electrician look for a faulty connection and correct the problem
410 | 108 | electrical | Electric Motors | motor overheating while running under load (continued) | high voltage | have an electrician check the terminals of the motor, using a voltmeter. make adjustments to lower the voltage
411 | 109 | electrical | Electric Motors | motor overheating while running under load (continued) | low voltage | have an electrician check the terminals of the motor, using a voltmeter. make adjustments to raise the voltage
412 | 109 | electrical | Electric Motors | motor overheating while running under load (continued) | rotor rubbing against the stator bore | check the machining. if the rubbing is due to bad machining practices, replace the bearings
413 | 110 | electrical | Electric Motors | motor vibrates after corrections have been made | motor misaligned | realign the motor
414 | 110 | electrical | Electric Motors | motor vibrates after corrections have been made | weak foundations | strengthen the base
415 | 110 | electrical | Electric Motors | motor vibrates after corrections have been made | coupling out of balance | dynamically balance the coupling
416 | 110 | electrical | Electric Motors | motor vibrates after corrections have been made | driven equipment out of balance | dynamically balance the driven equipment
417 | 110 | electrical | Electric Motors | motor vibrates after corrections have been made | bearings not in line | line up the bearings properly
418 | 110 | electrical | Electric Motors | motor vibrates after corrections have been made | defective ball bearing | replace the bearing
419 | 111 | electrical | Electric Motors | motor vibrates after corrections have been made | balancing weights shifted | dynamically rebalance the rotor
420 | 111 | electrical | Electric Motors | motor vibrates after corrections have been made | wound rotor coils replaced | dynamically rebalance the rotor
421 | 111 | electrical | Electric Motors | motor vibrates after corrections have been made | poly-phase motor running single-phase | check for an open circuit
422 | 111 | electrical | Electric Motors | motor vibrates after corrections have been made | excessive end play | adjust the bearing, or add a washer
423 | 112 | electrical | Electric Motors | unbalanced line current on poly-phase motors during normal operation | unequal terminal volts | have an electrician check the leads and connections and adjust as necessary
424 | 112 | electrical | Electric Motors | unbalanced line current on poly-phase motors during normal operation | single-phase operation | have an electrician check for open contacts
425 | 112 | electrical | Electric Motors | unbalanced line current on poly-phase motors during normal operation | poor rotor contacts in control wound rotor resistance | have an electrician check the control devices. correct the contacts
426 | 112 | electrical | Electric Motors | unbalanced line current on poly-phase motors during normal operation | brushes not in the proper position on the wound rotor | ensure that the brushes are properly seated and the shunts are in good condition
427 | 112 | electrical | Electric Motors | scraping noise | fan striking the insulation | clear the fan
428 | 112 | electrical | Electric Motors | scraping noise | fan rubbing against air shield | remove the interference
429 | 112 | electrical | Electric Motors | scraping noise | motor loose on the bedplate | tighten the hold down bolts
430 | 112 | electrical | Electric Motors | noisy operation | air gap not uniform | check and correct the bracket fits or the bearing
431 | 113 | electrical | Electric Motors | noisy operation (continued) | rotor unbalanced | dynamically balance the rotor
432 | 113 | electrical | Electric Motors | hot bearings | bent or sprung shaft | straighten or replace the shaft
433 | 113 | electrical | Electric Motors | hot bearings | excessive belt pull | decrease the tension on the drive belts
434 | 113 | electrical | Electric Motors | hot bearings | pulley too far from bearing | move the pulley closer to the motor bearing
435 | 113 | electrical | Electric Motors | hot bearings | pulley diameter too small | replace with larger pulleys
436 | 113 | electrical | Electric Motors | hot bearings | misalignment | correct the misalignment. realign the units
437 | 113 | electrical | Electric Motors | hot sleeve bearings | oil grooving in the bearing obstructed by dirt | remove bracket or pedestal with bearing. clean bearing housing and oil grooves. replace oil
438 | 113 | electrical | Electric Motors | hot sleeve bearings | oil viscosity too high | use recommended lighter oil
439 | 113 | electrical | Electric Motors | hot sleeve bearings | oil viscosity too low | use recommended heavier oil
440 | 114 | electrical | Electric Motors | hot sleeve bearings (continued) | too much end thrust | reduce the thrust that is induced by the driver. check the magnetic center of the motor
441 | 114 | electrical | Electric Motors | hot sleeve bearings (continued) | badly worn bearing | replace the defective bearing
442 | 114 | electrical | Electric Motors | hot anti-friction bearing | insufficient lubricant | maintain correct amount of lubricant in bearing
443 | 114 | electrical | Electric Motors | hot anti-friction bearing | excess lubricant | reduce the quantity of lubricant. /note/ reservoir should not be more than half full
444 | 114 | electrical | Electric Motors | hot anti-friction bearing | deterioration of the grease or contaminated lubricant | remove the old grease, wash the bearing thoroughly with kerosene, and replace with new grease
445 | 114 | electrical | Electric Motors | hot anti-friction bearing | overloaded bearing | check the alignment and the side and end thrusts
446 | 114 | electrical | Electric Motors | hot anti-friction bearing | broken ball or rough races | clean housing thoroughly. replace the bearing
447 | 115 | electrical | Electric Motors | overload on the driver | higher than design speeds | check the diameter of the sheaves to ensure that they are correctly sized for the unit. check the motor for the correct horsepower and loading. clear any obstacles
448 | 115 | electrical | Electric Motors | overload on the driver | belts rubbing hard against some projection | check lubrication practices. correct as required
449 | 116 | electrical | Electric Motors | overload on the driver (continued) | poor lubrication | collect a gas sample, and have engineering and chemistry check the gas analysis to determine the problem
450 | 116 | electrical | Electric Motors | overload on the driver (continued) | density of gas too high | ensure that the belt drive is not crossed. have the electricians check the rotation of the motor
451 | 116 | electrical | Electric Motors | overload on the driver (continued) | wrong rotational direction | when the fan is off, ensure that the unit is turned off the resting point periodically to prevent the shaft from sagging due to its own weight
452 | 116 | electrical | Electric Motors | overload on the driver (continued) | bent shaft | check for undue stress on the bearing mounts due to bad foundations and misaligned ductwork
453 | 117 | electrical | Electric Motors | overload on the driver (continued) | misalignment | ensure that the belts are sitting in their respective sheaves and are aligned to run true in the v-grooves. check the lineup of sidewalls of the sheaves with a straightedge or a stretched string. have electricians check wiring. check for overgreasing, especially on units that are greased by a pump grease gun
454 | 117 | electrical | Electric Motors | overload on the driver (continued) | motor phases wrongly wired | nan
455 | 117 | electrical | Electric Motors | overload on the driver (continued) | stator to air gap restricted | check the motor that has only a pedestal bearing with the other end connected to the coupling. /note/ the fan could be badly misaligned, which would affect the air gap between rotor and stator
456 | 118 | electrical | Electric Motors | overload on the driver (continued) | broken or cracked rotor bars | perform a vibration analysis. /note/ this problem will require major work and may require a new rotor
457 | 119 | electrical | Electric Motors (dc) | excessive sparking or flashing at brushes | rough commutator surface | sand or turn down
458 | 119 | electrical | Electric Motors (dc) | excessive sparking or flashing at brushes | low bar on commutator | grind or turn down balance of commutator
459 | 119 | electrical | Electric Motors (dc) | excessive sparking or flashing at brushes | high bar on commutator | if extreme, lower with a mallet blow and tighten clamp ring.. grind true
460 | 119 | electrical | Electric Motors (dc) | excessive sparking or flashing at brushes | high mica | undercut
461 | 119 | electrical | Electric Motors (dc) | excessive sparking or flashing at brushes | brushes too short | replace with harder grade — if worn too soon — and not by a rough commutator
462 | 119 | electrical | Electric Motors (dc) | excessive sparking or flashing at brushes | insufficient brush tension | adjust
463 | 119 | electrical | Electric Motors (dc) | excessive sparking or flashing at brushes | weak brush springs | replace
464 | 119 | electrical | Electric Motors (dc) | excessive sparking or flashing at brushes | brushes sticking in holders | free them. clean brushes if glazed
465 | 120 | electrical | Electric Motors (dc) | excessive sparking or flashing at brushes (continued) | dirt or oil on commutator | wipe clean. clean brushes if glazed
466 | 120 | electrical | Electric Motors (dc) | excessive sparking or flashing at brushes. blackened commutator | shortened armature winding | test for a short. do this after removing metallic contact between commutator bars. repair armature
467 | 120 | electrical | Electric Motors (dc) | intermittent sparking at brushes | open armature winding | locate and replace bad coil — or repair defective joint
468 | 120 | electrical | Electric Motors (dc) | fine dust under coupling employing rubber buffers or pins | misalignment | realign set
469 | 120 | electrical | Electric Motors (dc) | smoke, or solder 'whiskers' extending from the armature | overheating due to loose soldered connections that might cause future trouble | ensure all connections are tight. resolder all connections
470 | 121 | electrical | Electric Motors (dc) | motor will not start | usually a line problem | correct. check source of power supply. do not try to make the motor turn as it may burn up
471 | 121 | electrical | Electric Motors (dc) | motor will not start | load too heavy. disconnect motor to see if it starts without load | reduce load - or replace motor with unit of greater capacity
472 | 121 | electrical | Electric Motors (dc) | excessive humming sound | uneven air gap. measure with feeler gauge | replace bearings - before scraping noise indicates rotor is rubbing against stator
473 | 121 | electrical | Electric Motors (dc) | excessive humming sound | unbalanced rotor or bent shaft | check balance of rotor on parallel bars. check rotor tir. not to exceed +/- 0.002'
474 | 121 | electrical | Electric Motors (dc) | regular clicking noise | foreign matter in the air gap | remove the rotor and clean
475 | 121 | electrical | Electric Motors (dc) | rapid knocking | misalignment. magnetic center out of location | realign the set until knocking disappears. reset the magnetic center
476 | 122 | electrical | Electric Motors (dc) | brush 'chatter' | extreme motor vibration | determine source of vibration through analysis and correct problem
477 | 122 | electrical | Electric Motors (dc) | brush 'chatter' | vibration sources | misalignment. unbalance. bent shaft. resonance. oil whirl
478 | 122 | electrical | Electric Motors (dc) | vibration | misalignment | realign set
479 | 122 | electrical | Electric Motors (dc) | vibration | vibration in driven machine. run motor disconnected for check | eliminate source in machine, if possible. or change to a flexible belt drive may be in order
480 | 122 | electrical | Electric Motors (dc) | vibration | rotor out of balance | balance the rotor
481 | 123 | electrical | Electric Motors (dc) | motor overheating | overload | compare nameplate rating. check for excessive friction. reduce load. replace motor with one of a bigger capacity
482 | 123 | electrical | Electric Motors (dc) | motor overheating | dirt in motor | ensure sufficient airflow across motor. clean out dirt with a suitable solvent
483 | 123 | electrical | Electric Motors (dc) | motor overheating | rotor rubbing on stator | replace bearings
484 | 123 | electrical | Electric Motors (dc) | motor overheating | shorted stator windings | test with wattmeter and correct
485 | 123 | electrical | Electric Motors (dc) | motor overheating | ground | locate with a test lamp or growler and repair
486 | 124 | electrical | Electric Motors (dc) | bearing overheating | misalignment | realign set
487 | 124 | electrical | Electric Motors (dc) | bearing overheating | too much tension in chain or belt drive | reduce tension using the following formula: center span of belt deflection should be 1/64 inch per inch of centerline span between driver and driven units. chain deflection should be 2% of centerline span
488 | 124 | electrical | Electric Motors (dc) | bearing overheating | excessive end thrust | reduce thrust from driver or machine. ensure motor's magnetic center is correctly located
489 | 124 | electrical | Electric Motors (dc) | bearing overheating | too much grease (ball or roller bearings) | relieve supply to point set by the manufacturer
490 | 124 | electrical | Electric Motors (dc) | bearing overheating | sticking oil slinger ring | clean, repair, or replace
491 | 124 | electrical | Electric Motors (dc) | bearing overheating | insufficient lubricant | add to point set by the manufacturer
492 | 125 | electrical | Electric Motors (dc) | commutator hot | incorrect grade of brushes | replace with the proper grade
493 | 125 | electrical | Electric Motors (dc) | commutator hot | excessive brush pressure | decrease the brush spring tension
494 | 126 | electrical | Electrical Contacts | overheating | load current too high | reduce the load. use a larger contactor
495 | 126 | electrical | Electrical Contacts | overheating | loose connections | clean any discolored or dirty connections, and retighten them to the recommended torque setting
496 | 126 | electrical | Electrical Contacts | overheating | overtravel and/or contact force too low | adjust the overtravel as necessary. replace the contacts, and replace the contact springs as required to correct any defects
497 | 126 | electrical | Electrical Contacts | overheating | copper oxide or foreign matter collected on the contact faces | clean the contact surfaces, using a fine file or sandpaper. /note/ when performing this task in a dusty environment, use a dust-tight enclosure
498 | 127 | electrical | Electrical Contacts | overheating (continued) | load on in excess of 8 hours | change the operating procedure, and check with the factory for contacts more suitable for the length of use
499 | 127 | electrical | Electrical Contacts | overheating (continued) | ambient temperature too high | reduce the load. provide better ventilation. relocate the starter. use a larger contactor
500 | 127 | electrical | Electrical Contacts | overheating (continued) | line and/or load cables too small | replace with line and cables that meet the proper nec standards recommendation
501 | 127 | electrical | Electrical Contacts | welding of the contacts | overtravel and/or contact force too low | adjust the overtravel as necessary. replace the contacts, and replace the contact springs as required to correct the defect
502 | 127 | electrical | Electrical Contacts | welding of the contacts | contact bouncing on closing | correct the coil overvoltage condition. correct any mechanical defects
503 | 128 | electrical | Electrical Contacts | welding of the contacts (continued) | poor contact alignment | adjust contacts to touch simultaneously within 1/32' or to the manufacturer's specifications
504 | 128 | electrical | Electrical Contacts | welding of the contacts (continued) | jogging duty too severe | reduce the jogging cycle. use a larger contactor
505 | 128 | electrical | Electrical Contacts | welding of the contacts (continued) | excessive inrush current | readjust the accelerating time or the operating sequence. use a larger contactor
506 | 128 | electrical | Electrical Contacts | welding of the contacts (continued) | vibration in the starter mounting | insulate the starter from shock. provide a more rigid support for the starter
507 | 128 | electrical | Electrical Contacts | shorter contact life | low contact force | adjust the overtravel, replace the contacts, replace the contact springs, and set them to the correct contact force as necessary
508 | 128 | electrical | Electrical Contacts | shorter contact life | contact bouncing on opening or closing | correct the coil overvoltage condition. correct any mechanical defects
509 | 129 | electrical | Electrical Contacts | shorter contact life (continued) | abrasive dust on the contacts | clean and dress the contact faces in a dust-free environment. /caution/ do not use an emery cloth to clean and dress the contact faces. use glasspaper or a diamond file
510 | 129 | electrical | Electrical Contacts | shorter contact life (continued) | load current too high | reduce the load. use a larger contactor
511 | 129 | electrical | Electrical Contacts | shorter contact life (continued) | jogging cycle too severe | reduce the jogging cycle. use a larger contactor
512 | 129 | electrical | Electrical Contacts | shorter contact life (continued) | oil-immersed contactor being used instead of an air breaker contactor | replace with an air breaker contactor. /note/ an air breaker contactor may have 10 to 20 times longer contact life than an oil-immersed contactor of equal rating
513 | 130 | electrical | Electric Molded Case Breakers | frequent thermal nipping | excessive current | the breaker may be operating properly and clearing an overload. have an electrician check to see if the current is in excess of the thermal trip rating
514 | 130 | electrical | Electric Molded Case Breakers | frequent thermal nipping | terminals improperly torqued to the base of the breaker | visually inspect the breaker for discoloration that would indicate loose connections. have electricians torque the connections to the correct setpoint
515 | 131 | electrical | Electric Molded Case Breakers | frequent thermal tripping (continued) | cable improperly torqued in terminal | visually inspect the breaker for discoloration that would indicate loose connections. have the electricians check and correctly tighten the connections. /note/ machine vibrations can cause cables to loosen and can also cause cold flow when aluminum cables are used. cold flow refers to the contraction of the aluminum when the line is cooling down after the load is removed. this shrinkage can sometimes cause the connections to loosen
516 | 132 | electrical | Electric Molded Case Breakers | frequent thermal tripping (continued) | improper wire size | replace with the correct size wire. /note/ since the cable acts as a heat sink and carries heat away from the breaker, the proper wire size is important
517 | 132 | electrical | Electric Molded Case Breakers | frequent thermal tripping (continued) | ambient temperature too high | if the temperature fluctuates and frequently exceeds 140 °f, install an ambient compensating breaker
518 | 133 | electrical | Electric Molded Case Breakers | frequent thermal tripping (continued) | trip unit improperly torqued to base | remove the trip unit from the base, and inspect it for discoloration. reinstall the trip unit, and torque it to the base in accordance with the designed settings that come with each unit. /note/ a bright cherry red color indicates a temperature of approximately 1,450 °f for the trip unit. if the unit has experienced thermal damage, then it must be replaced
519 | 133 | electrical | Electric Molded Case Breakers | breaker tripping magnetically | high inrush current from the motor | adjust the magnetic trip rating to the next higher setting or until the breaker does not trip when the motor is started
520 | 134 | electrical | Electric Molded Case Breakers | breaker tripping magnetically (continued) | breaker tested with incorrect type of field testing | retest, using a six-cycle impulse test. /note/ a slow or gradual increase in current until the trip range is reached results in the breaker tripping at a lower value than that indicated on the trip unit. a six-cycle impulse test should be used. this is how the breakers are calibrated at the factory
521 | 135 | electrical | Electric Molded Case Breakers | breaker tripping magnetically (continued) | high peak current on y~delta starter transfer during open transition | close the open circuit. /note/ if an open circuit happens during transfer, the peak current during transfer could exceed 20 times the full-load amperes. /caution/ an extremely high magnetic trip setting can be supplied on the breaker, but the desired motor protection will be lost
522 | 135 | electrical | Electric Molded Case Breakers | mechanical and electrical malfunctions | high humidity | remove the breakers from high humidity locations since high humidity can cause dielectric and other problems associated with moisture. install heaters in the enclosure if the breakers cannot be removed from the humidity
523 | 136 | electrical | Electric Molded Case Breakers | mechanical and electrical malfunctions (continued) | corrosive environment | remove the breakers from corrosive environments if possible
524 | 136 | electrical | Electric Molded Case Breakers | mechanical and electrical malfunctions (continued) | attachments not functioning correctly | remove the cover from the breaker, and determine what type of attachment is fitted. ensure that the attachment is functioning correctly. ensure that the proper voltage is applied to an undervoltage release so that the breaker will operate when shunt trips are used. /warning/ ensure that the shunt trip is not energized while the operator is trying to close the breaker
525 | 137 | electrical | Magnetic Circuit | vibration and noise | low frequency, high voltage, core clamps slackened off during shipment or handling | adjust and secure the core clamps. if other problems exist, have a qualified electrician correct them
526 | 137 | electrical | Magnetic Circuit | overheating | high-input voltage | adjust and secure the core clamps. if other problems exist, have a qualified electrician correct them
527 | 137 | electrical | Magnetic Circuit | high exciting current | low frequency, high-input voltage | adjust and secure the core clamps. if other problems exist, have a qualified electrician correct them
528 | 137 | electrical | Magnetic Circuit | high core loss | low frequency, high-input voltage | adjust and secure the core clamps. if other problems exist, have a qualified electrician correct them
529 | 137 | electrical | Magnetic Circuit | insulation failure | very high core temperature due to high-input voltage or low frequency | adjust and secure the core clamps. if other problems exist, have a qualified electrician correct them
530 | 138 | electrical | Dielectric Circuit | smoke | insulation failure | inform electrical maintenance
531 | 138 | electrical | Dielectric Circuit | burned insulation | lightning surge | have them correct the condition
532 | 138 | electrical | Dielectric Circuit | burned insulation | broken terminals, taps, or arresters | repair or replace as necessary
533 | 138 | electrical | Dielectric Circuit | burned insulation | excessive dirt buildup or dust on the coils | clean the coils
534 | 138 | electrical | Dielectric Circuit | overheating | clogged air ducts | clean the air ducts
535 | 138 | electrical | Dielectric Circuit | breakers or fuses open | insulation failure | replace the insulation. reset the breakers or fires